# GARDEN GROVE SANITARY DISTRICT

GENERAL NOTES

- All main line sewer construction shall comply with the latest Standard Specifications and Standard Plans of the Garden Grove Sanitary District.

- The contractor shall secure a construction permit from the Garden Grove Sanitary District prior to the start of any construction and the District shall be notified (714) 741-5395 at least two (2) working days prior to starting work.

- Standard Plans and Specifications of the Garden Grove Sanitary District are available at the District Office, City Hall, Garden Grove, California.

- Sewer stationing does not necessarily coincide with street improvement stationing.

- All pipe, pipe joints and pipe fittings to be extra strength V.C.P. meeting all Federal Specifications SSP-3616 with wedge lock joints meeting A.S.T.M. Spec. D-425.  “No Hub” pipe with band seals is generally not permitted.  If “No Hub” pipe is allowed it must be installed with a joint seal with an additional stainless steel band to support the center of the joint.  District Inspector must approve installation prior to backfill.

- The use of Portland cement in joints is prohibited.

- Manholes shall be eccentric cone type, as shown on Standard Plans of the Garden Grove Sanitary District.  Manhole covers shall be 6” + below sub-grade and brought to grade when paving is complete.

- All manholes shall have an 8” stub (min.) each way.

- House lateral are shown approximate only and the exact location of wyes and laterals shall be determined in the field at the time construction except in cases where grade requires field control.

- Final air testing from pipeline leakage shall be made in the presence of the District Inspector after the District Engineer and the City Engineering Division have accepted backfill.

- Sewer pipes shall be balled in the presence of the District Inspector after final testing and manhole covers have been brought to grade upon completion of paving.  Detailed videotape shall be made of the sewer after testing and cleaning and a copy provided to the Sanitary District.

- The Engineer shall set top of curb stakes at house connections.

- The Contractor shall obtain a “City Right of Way Excavation” permit for work done in streets.

- Permit issuance is subject to payment of all necessary fees, and where applicable, granting the necessary easements to the Garden Grove Sanitary District and completion of the annexation process.

- The Engineer signing these plans shall be responsible for determining the correct locations and elevations of existing sewer facilities shown herein prior to construction.  All elevations shown shall be on the latest datum of the Orange County Surveyor.

- The sewer construction shall start at the connection of existing sewer facility and proceed upgrade.

- Prior to final acceptance, the Engineer signing the plans shall provide an “as-built plan” in autocad format including house lateral as required by the Sanitary District.

- Manholes left below grade shall be marked with a 4” x 4” redwood post painted white.

- The location of existing or proposed utilities is the responsibility of the Engineer signing the plans.  The District assumes no obligation for the existence or accuracy of any utilities.

- A grease trap is required per the California Plumbing Code for all establishments that serve or prepare food.

H\rj\sewernotes 2001

Rev (12/15/01